SPECIFICATIONS

TECHNICAL PROVISIONS

1.	GENERAL (MATERIAL & WORKMANSHIP)

1.1	All designs, equipments, materials and workmanship shall comply with and be tested in accordance with requirements of the Specifications.  Equipment or parts, which are not covered by the Specifications, shall comply with rules, codes and regulations of the International Electro-technical Commission or approved National Standardizing bodies. All necessary tests shall be performed to ensure that technical requirements are fulfilled.

1.2	The general intent of these Specifications is to require the supply of equipment and materials equal or superior to those actually described herein.  Unless otherwise stated, reference to the brand or manufacturer, if made, is only for the sake of comparison as to type, design, character or quality of the equipment and materials desired and shall not be interpreted as eliminating other equipment and materials of equal performance, quality and durability.

1.3	All dimensions and units given by the bidder in the bid and with its associated drawings and the drawings submitted by the contractor for approval shall be in metric system and all reference to weights, measurements and quantities shall be in metric units.

2.	SPECIFICATIONS AND DRAWINGS

2.1	The Contract shall be executed in strict conformity with the specification and/ or Drawings given or mentioned in this section and the Contractor shall do no ‘Work’ without proper Specification, Instructions and/or Drawings.

2.2	Specifications and/or drawings are intended to complement each other so that if any thing is shown on the drawings as required but not mentioned in the Specifications or vice versa, it shall be of like effect as if shown or mentioned in both.  If any errors, omissions or discrepancies are found in the figures, specifications and/or drawings or, if any feature shall appear to the Contractor to be indefinite or unclear, the same shall be referred to the Engineer whose written explanation and/or clarification shall be obtained before proceeding with the work.

2.3	Approval of the Engineer does not relieve the Contractor of his responsibility to do the work in accordance with the Contract.

2.4	The Contractor shall be responsible for any discrepancies, errors or omissions in any drawings or other particulars supplied by him whether such drawings or particulars have been approved by the Engineer or not.

2.5	All drawings and documents furnished by the Contractor in accordance with the Contract shall become the property of NTDC (WAPDA).

3.	TECHNICAL SPECIFICATIONS

3.1.	All the goods and equipment, the quantities of which are defined in Price Schedules, shall be of the material in accordance with the Technical Specifications appended hereto.

3.2.	Goods & material specified in the Technical Specification must comply with standards cited or other recognized standards, which ensure an equal or higher quality than the standards mentioned.

3.3.	Complete accessories such as danger plate, number plate, phase plates, anti climbing devices, barbed wire, U-Bolts, V-Shackles etc. shall be supplied alongwith towers.

3.4.         a)	U-Bolts for Suspension Strings shall be supplied by the towers manufacturer with the towers type E-A and V-Shackles for Tension Strings shall be supplied by the towers manufacturer with the towers type E-G whereas D-Shackles along with chain links  will be provided for tower type JKD.

b)	On WAPDA drawing No.EW/TF-11 “U-Bolt for Suspension String”, U.T.S. of this bolt may be read as 12000 Kg for EA Tower. Material of the U-Bolt shall be “drop forged steel hot dip galvanized. “Also Dimensions 70mm, 16mm & 19mm may be treated as binding dimensions and dimensions 120.5mm & 35mm may be treated as minimum.

c)	On WAPDA drawing No.EW/TF-12 “V-Shackle for Tension String”, U.T.S. of this shackle may be read as 20000 Kg, diameter of the bolt as M20 and grade of M20 bolt may be read as 10.9 for E-G Towers. Material of the V-Shackle shall be “drop forged steel hot dip galvanized”. Dia of the bolt i.e. 20 mm may be treated as non binding dimension. A Split Pin of Stainless Steel shall also be supplied with the bolt.

d)	On WAPDA drawing No. 216-12/328 “Shackle for conductor for tower type JKD” (or D-Shackle), grade of M24 bolt may be read as 8.8. Material of the D-Shackle and chain link shall be “drop forged steel hot dip galvanized”. Dia of the bolt i.e. 24 mm may be treated as non binding dimension. A Split Pin of Stainless Steel shall also be supplied with the bolt.

3.5	Hexagonal head bolts and hexagonal nuts shall be used with the towers. All connection bolts, nuts, lock nuts and washers of the towers shall be furnished at least 5% greater than actual to cope with losses and future maintenance, as defined in specification P-139:80.

3.6	All U-Bolts to be supplied with the towers shall be threaded for a sufficient length to take the standard nuts plus member & washer thickness.

3.7	The following standards may be used for fabrication of various towers to be supplied under the bidding document:

| Sr. No. | Description | Standard of Steel for Structure | Standard of Steel for Nuts & Bolts |
| --- | --- | --- | --- |
| 1. | Tower Type E-A, E-G & JKD. |  | ISO 898/ Grade 6.8 except where noted otherwise. |
|  | Member marked ‘H’ | ST 52 or equivalent |  |
|  | Other members | ST-42 or equivalent |  |

All Nuts and Bolts to be supplied with Towers shall be of grade as specified and shall be of M16, M20 or M24 as mentioned on drawings. One full set of bolt includes one bolt, one plain washer (5mm thick), one nut and lock nut. The length of bolts given on drawings shall also be increased accordingly as given on drawings to accommodate Lock Nuts. The dimensions of bolts, plain washers, nuts and lock nuts shall be as per following standards

| Sr.No. | Description | Standard to be used for dimensions |
| --- | --- | --- |
| 1. | Bolts | DIN 7990 |
| 2. | Plain Washers | DIN 126 |
| 3. | Nuts | DIN 555 |
| 4. | Lock Nuts | DIN 936 |

Sampling and testing of nuts & bolts shall be carried out as per             ISO-898/ASTM A-394.

Note:	No substitution of members’ sizes in the original design of towers will be entertained.

3.8	Washers shall not be less than 5mm thickness for tower type EA, EG & JKD. Only one thickness of washer shall be used. The diameter of washer hole shall be 1.6mm larger than the bolt diameter and the outside diameter of the washer shall not be less than 1.6mm larger than the diagonal of the nut.

3.9	OPGW HARDWARE ACCESSORIES

- The material of steel components of OPGW hardware accessories will be “drop forged high quality Galvanized steel” conforming to latest ANSI standards.

- For testing, sampling, acceptance & rejection, marking and packing and information to be supplied, Clause No.7,8,9,10,11,13,14 and 15 of specification P-141:80 (Transmission lines Earth Wire Fittings) are to be followed.

3.10	The following Technical Specifications are applicable along with the amendments given under clause 3.10 hereafter:

1.	Specifications for Towers

1.1	220 kV Transmission Line Towers	(P-163: 82)

(Including Amendment No. 1, dated 15th April 1985)

1.2	Fabrication of Steel Structures 	(P-139: 80)

(Including Amendment No. 1, dated 3rd October 1982)

1.3	Zinc Coatings 	(P-82: 81)

1.4	Barbed Wire (Including Amendment No.1 dated 5th Jan.	       (P-162:81)

1989)

1.5	Danger and Sign Plates (Including Amendment No.1       (P-104:76)

dated 12th  December 1981)

1.6	Plain Steel Washers					       (P-20:68)

2.	Specifications for Conductor and Shield Wire

2.1	Aluminium Conductors, Steel – Reinforced 	(P-50: 88)

(Including Amendment No. 1, dated 12th February 1990)

2.2	Galvanized Steel Wires 	(P-12: 80)

(Including Amendment No. 3, dated 26th February 1985)

3.	Specifications for Insulators and Hardware

3.1	Disc Type Porcelain Insulators 	(P-8: 96)

3.2	Suspension Strings for Two Conductor Bundle 	(P-187: 91)

3.3	Tension Strings for Two Conductor Bundle 	(P-188: 91)

4.	Specifications for Conductor and Shield Wire Accessories and Dampers

4.1	Mid Span Joints and Repair Sleeves for Transmission Lines 	(P-144: 80)

(Including Amendment No. 1, dated December 1982)

4.2	Spacer Dampers for Two Conductor Bundle 	(P-189: 89)

4.3	Stock Bridge Vibration Dampers	   (P-142:83)

(Including Amendment No. 1, dated 25th November 1990)

5	Specifications for Grounding Material

5.1	Earth Rod 	(P-116: 81)

5.2	Copper Wire for Earthing 	(P-16: 68)

6.	Specifications for OPGW, Joint Boxes, Hardware, Accessories & Dampers:

Note:		The updated specifications will be applicable.

3.11		The following Amendments in Specifications may please be incorporated:

A)	220 KV TRANSMISSION LINE TOWERS 	(P-163: 82)

- The clauses related to design of 220KV Towers will not be applicable as the towers are to be fabricated only as per drawings enclosed under Volume-3 of this bidding document. However, in accordance with these drawings, the contractor shall submit detailed manufacturer’s towers fabrication/assembly drawings for approval by the engineer before taking the manufacturing/fabrication work in hand by his manufacturer.

- U-Bolts & V-Shackles shall be supplied as per clause 3.4 at page TP-3 herein above.

B)	FABRICATION OF STEEL STRUCTURES (P-139:80)

Please replace clause 8.3 with the following:

Check Assembly of Towers

Before proceeding with the bulk fabrication of any type of tower, the Contractor shall fabricate and assemble in his works for inspection by the purchaser or his authorized representative, one tower of each type as finally approved by the Purchaser for checking the fabrication accuracy and workmanship. The check assembly shall be preferably in vertical position. In case of assembly in horizontal position, the complete tower assembled along with body/leg extensions shall be adequately supported to prevent distortion and overstressing of members to ensure proper fit and shall be accomplished without extraordinary effort to align bolt holes or to force pieces into position. For the check assembly, bolts and nuts shall be not more than finger tight. The members and nuts, bolts, lock nuts, washers, fillers etc. used in prototype assembly shall be of the same grade & size/dimensions specified in the approved drawings and to be supplied against the respective contract/purchase order.

C) 	SPACER DAMPERS FOR TWO CONDUCTOR BUNDLE (P-189:89)

- Clause 3.2, Table II, Page-2

  - For ACSR Rail, read Average Span Length as ‘370m’  instead of existing ‘400m’  and read No. of spacer dampers per span ‘5’ instead of existing ‘6’

  - Delete first sentence of ‘Note’ given at the end of this table.

- Clause 4.9, Page-5

- In line 14 of this clause, read “-30ºC to +75ºC” instead of “-5ºC to 75ºC”.

- In line 18 of this clause, the existing words “atmospheric dust particles” may be replaced with the words “dust particles and other atmospheric contaminants”.

- Clause 6.2, Page-6

  - In line 3 of this clause, read “40,000 Amps” instead of existing “10,000 Amps”.

- Add the following new clause 7.4 after clause 7.3 at page-7:

“7.4	This guarantee in respect of system performance is applicable under the basic line data and environmental conditions prevailing in the area.”

- Clause 8.1.2.1, Page-7

  - In line 2 of this clause, add the words “tensioned to approximately 17% of its rated strength” after the word “clamp”.

- Clause 8.1.4.(b), Page-9

a)	In line 1 of this sub clause, read “8.75” instead of existing “3.75”.

- Add the following new clause 8.1.4.(A) after clause 8.1.4. at page-9:

“8.1.4.(A)	Conical Fatigue Test

The same spacer damper used in test under clause 8.1.4. shall be tested for conical fatigue by fixing the central frame and installing the clamp on a cylindrical bar of dia equal to the specified conductor dia. The clamp shall be excited through rotation so that a conical movement is achieved. The angle between the conical surface of the revolution generated by the cylindrical bar and the longitudinal axis of the clamp shall not be less than 2 degrees. The test shall be performed for 1 million cycles at frequency between 2 to 5 Hz. After the test, there should be no damage to any of the components or loosening of the bolt.”

- Clause 8.1.8.1, Page-10

  - In line 2 of this clause, read “40,000 Amperes” instead of existing “10,000 Amperes”.

- Clause 8.1.8.2, Page-10

  - Add the following sentence at the end of this clause:

“After the test, there shall no indication of failure of any component or any permanent deformation from the original geometric configuration.”

- Clause 8.1.9.2, Page-10

  - In line 4 of this clause, add the words “in horizontal configuration” after the word “bundle”

- Add the following new clause 8.1.10 after clause 8.1.9.4 at Page-10:

“8.1.10		Ozone Resistance

Non-Metallic Spacer damper parts shall resist Ozone attack and shall show no sign of damage after the following Ozone test as per ASTM D-1149 modified as follows:

Two finished full size specimens, mounted in their normal housing will be placed in an Ozone chamber for 70 hours at a temperature of 60ºC. The concentration of Ozone shall be 50 parts per 100 million. One specimen shall be unstressed, and the second specimen will be subjected to the maximum stress.

No cracks shall be visible under 7x Magnification.”

- Clause 8.2, Sample Test

a)	Add the following at the end of this clause:

“vi)	Fault Current/Short Circuit Test”

- Add the following new clause 8.2.6 after clause 8.2.5 at Page-11:

“8.2.6 		Fault Current/Short Circuit Test

As given in clause 8.1.8.”

- Table-III Sample Size

a)	Line 3&4 of the title of middle column may be read as “Clause 8.2.3, 8.2.4, 8.2.5 & 8.2.6” instead of existing “Clause 8.2.3, 8.2.4 & 8.2.5.”

D)	STOCK BRIDGE VIBRATION DAMPERS (P-142: 83)

i)	Clause 3.2 Table II

a)	Read No. of Dampers per Span of ACSR Rail & OPGW as “2” instead of “1” in this table.

- Delete text given under “Note” at the end of this table.

ii)	2 dampers per span of ACSR Rail & OPGW should be designed installing one damper on each end of the span for average span length of 370m. Contractor shall ascertain the dampers spacing and the number required in accordance with the sag- tension, span lengths and environmental conditions of the site.

A drawing showing dampers location for various span lengths along with its distance of installation shall be submitted with the bid.

iii)	Clause 4.1

a)	Add the following text at the end of this clause:

“The clamping area shall be such that damper neither slips nor damage the conductor/overhead shield wire. When installed at the recommended torque, the clamp shall not slip below 250 & 150Kg force for conductor and shield wire dampers respectively. The clamps of vibration dampers shall be able to withstand a bolt torque equal to 150 percent of nominal design installation torque.”

iv)	Clause 4.2

- Add the following sentence at the end of the clause:

“Break away bolts shall be required for dampers”.

- Add the following new clauses 5.1.4 to 5.1.8 after clause 5.1.3:

“5.1.4	The following tests shall be performed on each of at least two assemblies selected at random and performed in the order prescribed below.

“5.1.5		Clamp Slippage Test at Ambient Temperature.

The test shall be carried out on a length of specific conductor/shield wire tensioned at E.D. Stress given in table-II. The vibration damper shall be installed on the conductor in accordance with manufacturer installation instructions by applying a tightening torque on the upper head of break-away bolt until breakage of the upper head occurs. The relevant torque shall be recorded. Then a load of 250Kg for conductor or 150 Kg for shield wire shall be applied to the clamp parallel to the axis of conductor/shield wire and held for minimum 1 minute without initial slip. The initial slip load is defined as the load at which the clamp moves 0.5mm or more on the conductor/shield wire. The load shall be increased until the continual slip occurs. The relevant value shall be recorded.

5.1.6.		Bolt Torque Test

The test shall be carried out on the samples submitted to above test. After completion of the above test, a torque of 150 percent of nominal design installation torque shall be applied at lower head of the bolt in order to see that there shall be no failure of component parts. Records shall be made of the lower head withstand torque, failure torque and the part(s) of the clamp assemblies that fail.

    - Corona Test

The corona extinction voltage for the stock bridge vibration dampers shall be determined visually in a virtually dark laboratory. The corona extinction voltage is the voltage at which the damper is free of all visual corona.

The vibration dampers type SB-R shall be installed on section of ACSR “Rail” conductor or bar of equivalent diameter. The conductor or bar shall be arranged in the configuration similar to be used in the field.

The vibrations dampers shall be subjected to a voltage determine that the corona extinction voltage level is not less than 160KV line to ground. The ground plane shall be a maximum of 4 meters from the assembly.

The exposure shall be made with an applied voltage and the laboratory virtually dark. There shall be no evidence of corona on the Vibration dampers.

    - The R.I.V. level shall be measured in accordance with NEMA Standard with the samples used for corona test.”

- Clause 5.2, Sample Test

  - Add the following at the end of this clause:

“iv) 	Clamp slippage Test at Ambient Temperature

v)	Bolt Torque Test”

- Clause 6, TEST METHODS

  - Read title of this clause as “TEST METHODS FOR SAMPLE TESTS” instead of “TEST METHODS”.

- Add the following new clauses 6.4 and 6.5 after clause 6.3:

6.4		Clamp Slippage Test at Ambient Temperature

As given in clause 5.1.5.

6.5		Bolt Torque Test

As given in clause 5.1.6.

- TABLE-III, Page-5

  - Line 3 of the title of middle column may be read as “in Clause 6.3, 6.4 & 6.5” instead of existing “in Clause 6.3”.

F)	DISC TYPE PORCELAIN INSULATORS (P-8:96)

- Clause 8.1.5, Page-10

- In line 5&6 of this clause, read “-15 deg. C. to +55 deg. C.” after the word “from” instead of “-5 deg. C. to 65 deg. C.”

- Please replace Clause 8.1.8, page 11 with the following:

    - Power Arc Test

      - For power arc test, insulators shall be selected at random from the first lot.

      - The power arc test shall be performed in accordance with the IEC- 61467 for short string insulators. The results thus obtained should comply with the acceptance criteria of IEC 61467.

G)	ALUMINUM CONDUCTOR STEEL REINFORCED (P-50:88)

- Add following clause before clause 9 in the specification:

9a.)	Tests

9a.1)	Type tests

The following type tests shall be carried out in accordance with clauses and standards mentioned against each

| 1. | Stress strain test | IEC 61089 & IEC 61395 |
| --- | --- | --- |
| 2. | Tensile test on composite conductor | IEC 61089 |
| 3. | Joints in Aluminum wires | IEC 61089 |

9a.2)	Sample tests

The following sample tests shall be performed on the offered type of conductor in accordance with WAPDA specification P-50:88, supplemented by applicable IEC, ASTM Standards.

| 1. | Visual examination |
| --- | --- |
| 2. | Verification of dimensions |
| 3. | Measurement of lay ratio of each layer |
| 4. | Tensile test on whole conductor |
| 5. | Breaking load of individual wires |
| 6. | Wrapping test |
| 7. | Resistivity test on aluminum wires |
| 8. | Stress at 1% extension of steel wires |
| 9. | Bend test |
| 10. | Ductility test |
| 11 | Galvanizing tests |

Sample test # 1, 2, 3 & 9 shall be performed as described below and supplemented by applicable IEC & ASTM standards.

- Visual Examination

The conductor shall be examined visually for good workmanship and general surface finish and shall generally conform to the requirements of the specification. The conductor will be initially checked  for any scratches, joints, burrs, indentation, black and bare spots,  projections, slackness, spacing between the individual wires, bird caging etc.,.  The offered Lot will be rejected if any of the above mentioned defects persist in the length of the conductor.

The conductor reels shall be visually and dimensionally checked to ensure that they confirm to the requirements of this specification. The reels shall be of sound construction and properly seasoned. Wet or termite effected reels will be rejected. Thick paper board shall be applied inside the flange and polypropylene sheets shall be applied on the drum of the wooden reels before winding of the conductor on the reels to avoid damage to the conductor. Polyethene sheets shall be wrapped over the conductor after winding. The reels without these accessories will be rejected.

The conductor will be wound on reels in a way so as to avoid scratching during re-winding of conductor; as such scratching persistently existing will result in rejection of conductor on that reel.

- Verification of Dimensions:

The diameters of individual Aluminum & Steel Wires, diameter of complete conductor, unit weight of conductor etc., shall be checked by selecting 10% of the material of a given Lot.

To check the weight and complete length of conductor (as specified in the specifications) on a certain reel, 5% of the reels shall be selected from the offered Lot. The reels with conductor shall first be checked for weight, the conductor shall be completely rewound from the reel and the weight of the empty reel will be taken again to check the total weight of the conductor on the reel.

All the results shall confirm to the values specified in the specifications and any variations will only be allowed as per the tolerances specified, beyond which, the material will be rejected.

- Measurement of Lay-Ratio of Each Layer:

The lay-ratios of each layer of the conductor shall be measured and checked to ensure that they conform to the requirements specified in clause 8 and table-VI of this specification.

- Bend Test

For bending properties, five percent (5%) of the reels shall be checked. The bending properties shall be ensured by rewinding of the conductor. The samples selected under clause (B: verification of dimensions) may be used for this test also.

During rewinding, the conductor shall be checked for any kinks, stresses, broken strands and the defects mentioned in clause (A: Visual Examination). The presence of any of the aforementioned defects will result in the rejection of the whole Lot offered for inspection.

- Add the following paragraph at the end of clause 6.4.4:

Strength of Conductor

Before starting the test, circles perpendicular to the axis of the conductor shall be marked at two places on the sample of conductor. The load shall be increased at a steady rate up to 50% of minimum specified UTS and held for one minute. The circles drawn shall not be distorted due to relative movement of strands. Thereafter the load shall be increased at steady rate to 95% of UTS and held for one minute. The Conductor sample shall not fail during this period. The applied load shall then be increased until the failing load is reached and the value recorded

H)	SUSPENSION STRINGS (P-140:82)

Add the following at the end of Clause 7.1.

- Power Arc Test 	For complete insulator string

Add the following at the end of Clause 10.

Power Arc Test

The power arc test shall be performed in accordance with IEC 61467 for test series “X” on complete hardware assembly.

I)	TENSION STRINGS (P-143:82)

Add the following at the end of Clause 7.1.

- Power Arc Test 	For complete insulator string

Add the following at the end of Clause 14.

Power Arc Test

The power arc test shall be performed in accordance with IEC 61467 for test series “X” on complete hardware assembly including compression dead end splices.

J)	SUSPENSION STRINGS FOR TWO CONDUCTORS BUNDLE (P-187:91)

Add the following at the end of Clause 7.1.

- Power Arc Test 	For complete insulator string

Add the following at the end of Clause 10.

Power Arc Test

The power arc test shall be performed in accordance with IEC 61467 for test series “X” on complete hardware assembly.

K)	TENSION STRINGS FOR TWO CONDUCTOR BUNDLE (P-188:91)

Add the following at the end of Clause 7.1.

- Power Arc Test 	For complete insulator string

Add the following at the end of Clause 14.

Power Arc Test

The power arc test shall be performed in accordance with IEC 61467 for test series “X” on complete hardware assembly including compression dead end splices.

L) 	OPGW HARDWARE ACCESSORIES

For OPGW accessories: add following

OPGW HARDWARE ACCESSORIES

- The material of steel components of OPGW hardware accessories will be “drop forged high quality Galvanized steel” conforming to latest ANSI standards.

- For testing, sampling, acceptance & rejection, marking and packing and information to be supplied, Clause No.7,8,9,10,11,13,14 and 15 of specification P-141:80 (Transmission lines Earth Wire Fittings) are to be followed.